|  | Name | Signature | Date |
| --- | --- | --- | --- |
| Prepared by: |  |  |  |
| Authorised by Production Manager, or delegate |  |  |  |
| Approved by Quality Manager, or delegate |  |  |  |

# Purpose

## This Validation Protocol is for the purpose of temperature mapping critical material storage areas to determine whether they are able to maintain temperatures suitable for the storage of critical material. Temperature mapping is to be performed according to [client document number].

# References:

# Insert list of referenced documents here

# Definitions:

# Insert list of referenced terms and acronyms here

# Validation Plan

Answers to the questions below (in blue) are to be inserted in to the Validation Report.

| Environmental conditions | List any factors affecting the ability of the area to maintain temperature (e.g. air-flow, or air-balance? |
| --- | --- |
| Heat sources | Validation is to be performed encompassing a period during routine working hours. Staff access is not to be restricted. All equipment in the area is to be operational during routine hours. Are there any specific heat sources which may have an effect on the temperature of the area to be mapped? (For example, is the cupboard close to an incubator?) |
| Temperature monitoring | How is the area to be temperature monitored? |
| Load conditions (Critical Material Storage only). | Map the critical material storage area, at both empty and full capacity. |
| Environmental control system. | Is the area to be mapped environmentally controlled and alarmed? 24/7, or just during routine working hours? What are the current alarm set points? |

| Duration of Temperature Mapping Activity | Data-Logger timing intervals |
| --- | --- |
| What is the total time period over which the mapping will be conducted and will it be conducted during working hours? | Record interval time here. |

# Determination of data-logger locations

When determining data-logger locations, make sure that loggers are positioned near heat sources and opening doors, and that there is a data-logger at, or near the probe location if monitored by a Building Management System or similar).

Record the data-logger locations in the Validation Report.

# Method

| # Step | # Description |
| --- | --- |
| # 1 | # Obtain calibration certificates of Data-loggers and check that they are in-date |
| # 2 | ## Check that the timing intervals of the data-loggers are correct. |
| # 3 | ## Place Data-loggers in the area to be mapped, and record their numbers and positions. Data-logger Numbers’ and positions are to be diagrammatically represented in the Validation Report. Make sure that if the area is monitored by a Building Management System or similar system, that a data-logger is placed as near as possible to the Building Management System probe and record this on the diagram /s. The type of logger used is also to be noted in the Validation report |
| # 4 | ## Leave the data-loggers in position for the required time-frame. For mapping of a critical material storage area, take note of the day and time that the load is changed from empty to full. |
| # 5 | ## Download the data-loggers at the completion of the validation and save the data. |
| # 6 | ## Analyse the data and record the results as per the Validation Temperature Mapping Report Template. |

# Validation Report

The Temperature Mapping Validation Report template must be used to write the temperature mapping report. Complete all sections as instructed. Extra information may be included in the report if required.

# Document Change History Record

| Document Owner |  |
| --- | --- |

| Version Number | Section Amended | Amendment Details | Date of Approval |
| --- | --- | --- | --- |