## Acceptance Criteria
Environmental Monitoring Results
Document No Version NO | [7 empty] | Active:
Author:
Refer to Environmental Monitoring SOP for the procedure for completion of this form
Microbial Specifications for Viable Air Monitoring, Settle Plates, Swabs and Contact Plates
Environmental Grade | Maximum allowed CFU per sample
| Air Sample |  | Settle Plates (diam. 90mm) |  | Contact plates |  | Swabs
| cfu/m3 |  | cfu/4 hours* |  | (diam. 90mm) |  | cfu/plate
cfu/plate
| Alert | Action | Alert | Action | Alert | Action | Alert | Action
A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B | 5 | 10 | 2 | 5 | 2 | 5 | 2 | 5
C | 50 | 100 | 25 | 50 | 12 | 25 | 12 | 25
D | 100 | 200 | 50 | 100 | 25 | 50 | 25 | 50
Particulate Air Monitoring Specifications
Acceptance Criteria
Room Grade | At-Rest |  | Operational
| (part/m3)* |  | (part/m3)*
| 0.5µm | 5.0µm | 0.5µm | 5.0µm
A | 3520 | 20 | 3520 | 20
B | 3520 | 29 | 352000 | 2900
C | 352000 | 2900 | 3520000 | 29000
D | 3520000 | 29000 | N/D | N/D
Personnel Monitoring Specifications
Personnel Monitoring Type | CFU
| Alert Limit | Action Limit
Hood | ≤3cfu | ≤5cfu
Chest | ≤3cfu | ≤5cfu
Sleeve | ≤3cfu | ≤5cfu
Gloves | ≤3cfu per glove | ≤5cfu per glove

## At-Rest
Environmental Monitoring Results
Document No. Version No. | [7 empty] | Active:
Author:
Refer to Environmental Monitoring SOP for the procedure for completion of this form
Env. Grade
Air (viable) Monitoring
Date
Cleanroom BSC 1 | A
Cleanroom BSC 2 | A
Cleanroom BSC 3 | A
Cleanroom Work Bench | C
Ante-room | C
Negative Control
TSA Batch No. & Expiry
Operator Initials & Date
Comments / Observations
Env. Grade
Surface Monitoring
Date
BSC 1 - Wall | A
BSC 1 -Base | A
BSC 1 - Floor (Under Bench) | C
BSC 2 - Wall | A
BSC 2 - Base | A
BSC 2 - Floor (Under Bench) | C
BSC 3 - Wall | A
BSC 3 - Base | A
BSC 3 - Floor (Under Bench) | C
Cleanroom Work Bench | C
Consumables Trolley | C
Consumables Trolley | C
Microscope Trolley | C
Centrifuge 1 | C
Centrifuge 2 | C
Incubator 1 | C
Incubator 2 | C
Incubator 3 | C
Incubator 4 | C
Fridge 1 | C
Fridge 2 | C
Ante-room Floor | C
Ante-room Work Bench | C
Pass-Through Hatch | D
Change Room Clean | D
Change Room Dirty | E
Negative Control
Rodac Batch No. & Expiry
Operator Initials & Date
Comments / Observations
Env. Grade
Particulate (non-viable) Monitoring
|  | 0.5µm | 5.0µm | 0.5µm | 5.0µm | 0.5µm | 5.0µm | 0.5µm | 5.0µm | 0.5µm | 5.0µm | 0.5µm | 5.0µm | 0.5µm | 5.0µm | 0.5µm | 5.0µm
Date
BSC 1 | A
BSC 2 | A
BSC 3 | A
Cleanroom Outlet 1 | C
Cleanroom Outlet 2 | C
Cleanroom Inlet | C
Ante-room Outlet | C
Ante-room Inlet | C
Operator Initials & Date
Comments / Observations

## In-Process
Environmental Monitoring Results
Document No. Version No. |  |  | Active:
Author:
Refer to Environmental Monitoring SOP for the procedure for completion of this form
STAGE 1
Env. Grade
Major Process Settle Plates
Date
Process Type
BSC 1 - Left | A
BSC 1 - Right | A
BSC 2 - Left | A
BSC 2 - Right | A
TSA Batch No. & Expiry
Exposure Time (In/Out)
Operator Initials & Date
Comments / Observations
Env. Grade
Major Process Contact Plates
Date
Centre of BSC 1 | A
Centre of BSC 2 | A
Centre of BSC 3 | A
Incubator 1 | C
Incubator 2 | C
Incubator 3 | C
Incubator 4 | C
Rodac Plates Batch No. & Expiry
Operator Initials & Date
Comments / Observations

## Personnel Monitoring
Environmental Monitoring Results
Document No. Version No. | [7 empty] | Active:
Author:
Refer to Environmental Monitoring SOP for the procedure for completion of this form
Personnel Monitoring
|  |  |  | Results |  |  |  | TSA Batch No. & Expiry | Rodac Batch No. & Expiry | Comments
Name | Date | Process Type | Process ID | Hood | Chest | Sleeve | Gloves

## Retests
Environmental Monitoring Results
Document No. Version No. |  |  |  |  | Active:
Author:
Refer to Environmental Monitoring SOP for the procedure for completion of this form
Facility | Retest Location | Air/Surface | Date | Result | TSA Batch No. & Expiry | Rodac Batch No. & Expiry

## Incubator Water
Environmental Monitoring Results
Document No. Version No. |  |  |  | Active:
Author:
Refer to Environmental Monitoring SOP for the procedure for completion of this form
Incubator Number | Location | Date | Result | R2A Batch No. & Expiry

## Comments & Observations
Environmental Monitoring Results
Document No. Version No. |  |  | Active:
Author:
Refer to Environmental Monitoring SOP for the procedure for completion of this form
Comment/Observation Number | Comment/Observation
1
2
3
4
5
6
7
8
9
10
11
12